## Sheet
Canopy Commissioning Report
CLIENT:
PROJECT NAME:
PROJECT NUMBER:
DATE OF VISIT: 2025-01-26
ENGINEER(s):
KITCHEN CANOPY AIR READINGS
EXTRACT AIR DATA
Drawing Number:
Location:
Model: KVF
Total Design Airflow: 1.8 m³/s
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 40.0 Pa |  | 71.8 |  | 454.0 | 0.13 | 7.0%
Total Flowrate 0.13 m³/s
Total Percentage 7.0%
SUPPLY AIR DATA
Drawing Number:
Location:
Model: KVF
Total Supply Design Airflow: 0.0 m³/s
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
SUPPLY AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 0.0 Pa |  | 121.7 |  | 0.0 | 0.0
Total Flowrate 0.0 m³/s
Total Percentage 0%
RESULTS SUMMARY - EXTRACT AIR
Drawing Number |  | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
|  | 1.8 m³/s |  | 0.13 m³/s |  | 7.2%
TOTAL |  | 1.8 m³/s |  | 0.13 m³/s |  | 7.2%
RESULTS SUMMARY - SUPPLY AIR
Drawing Number |  | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
TOTAL |  | 0 |  | 0 |  | 0%
ADDITIONAL NOTES
Date |  | 2025-01-26
Print
Sign