## Sheet
Canopy Commissioning Report
CLIENT: Yazan Hunjul
PROJECT NAME: 123 Main St
PROJECT NUMBER: Azzam Hunjul
DATE OF VISIT: 2025-05-06
ENGINEER(s): Yazan Hunjul
Your Kitchen Ventilation System has the following serviceable technology:
KITCHEN CANOPY AIR READINGS
EXTRACT AIR DATA
Drawing Number | 12345-1929
Canopy Location | Main Kitchen
Canopy Model | CMW-FMOD
Design Flowrate (m³/s) | 1.2
Quantity of Sections | 2
Length of Slot (mm) | 1000
Width of Slot (mm) | 85
Calculation | Qv = k x √PTAB
With M.A.R.V.E.L. | Yes
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) | K-Factor (m³/h) | Flowrate (m³/h) | Flowrate (m³/s) | Min (%) | Idle (%) | Design (m³/s)
1 | 20.0 | 115 | 514 | 0.143 | 30.0% | 70.0% | 0.0
2 | 50.0 | 115 | 813 | 0.226 | 30.0% | 70.0% | 0.0
Total Flowrate: 0.369 m³/s
EXTRACT AIR DATA
Drawing Number | 1.27
Canopy Location | Main Kitchen
Canopy Model | CXW
Design Flowrate (m³/s) | 1.3
Quantity of Grills | 2
Grill Size | 350x300 mm
Calculation | Qv = A x v
With M.A.R.V.E.L. | Yes
EXTRACT AIR READINGS
Grill # | Anemometer Reading (m/s) | Free Area (m²) | Flowrate (m³/h) | Flowrate (m³/s) | Min (%) | Idle (%) | Design (m³/s)
1 | 30.0 | 0.105 | 11340 | 3.15 | 20.0% | 70.0% | 0.000
2 | 32.0 | 0.105 | 12096 | 3.36 | 50.0% | 70.0% | 0.000
Total Flowrate: 6.510 m³/s
EXTRACT AIR DATA
Drawing Number | 123455-9128
Location | Second Kitchen
Model | UVF
Design Airflow (m³/s) | 1.2
Quantity of Sections | 1
Calculation | QV = Kf x √Pa
With M.A.R.V.E.L. | Yes
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) | K-Factor (m³/h) | Flowrate (m³/h) | Flowrate (m³/s) | Min (%) | Idle (%) | Design (m³/s)
1 | 40.0 Pa | 71.8 | 454.0 | 0.126 | 28.0% | 80.0% | 1.2
Total Flowrate: 0.126 m³/s
SUPPLY AIR DATA
Drawing Number | 123455-9128
Location | Second Kitchen
Model | UVF
Design Airflow (m³/s) | 1.1
Quantity of Sections | 1
Calculation | QV = Kf x √Pa
With M.A.R.V.E.L. | Yes
SUPPLY AIR READINGS
Section # | T.A.B Point Reading (Pa) | K-Factor (m³/h) | Flowrate (m³/h) | Flowrate (m³/s) | Min (%) | Idle (%) | Design (m³/s)
1 | 30.0 Pa | 121.7 | 666.58 | 0.185 | 34.0% | 50.0% | 1.8
Total Flowrate: 0.185 m³/s
UV CAPTURE RAY SYSTEM FOR UVF
Quantity of Slaves per System | [5 empty] | 2
UV Pressure Setpoint (Pa) | [5 empty] | 23
Capture Jet Average Pressure Reading (Pa) | [5 empty] | 0
Airflow Proved on Each Controller | [5 empty] | ✓
Communication To All Canopy Controllers | [5 empty] | ✓
UV System Tested and Fully Operational | [5 empty] | ✓
All UV Safety Switches Tested | [5 empty] | ✓
All Filter Safety Switches Tested | [5 empty] | ✓
RESULTS SUMMARY - EXTRACT AIR
Drawing Number | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
12345-1929 | 1.200 |  | 0.369 |  | 30.8%
1.27 | 1.300 |  | 6.510 |  | 500.8%
123455-9128 | 1.200 |  | 0.126 |  | 10.5%
TOTAL | 3.700 |  | 7.005 |  | 189.3%
RESULTS SUMMARY - SUPPLY AIR
Drawing Number | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
12345-1929 | 1.100 |  | 0.000 |  | 0.0%
123455-9128 | 1.100 |  | 0.185 |  | 16.8%
TOTAL | 2.200 |  | 0.185 |  | 8.4%
FINAL SYSTEM CHECKS
EDGE BOX
Edge Installed | [5 empty] | ✓
Edge ID | [5 empty] | 1234-1255
Edge 4G Status | [5 empty] | Online
LAN Connection Available | [5 empty] | Yes
Modbus Operation
ADDITIONAL NOTES
All Good
Date | 2025-05-06
Print | Yazan Hunjul
Sign