## Sheet
Canopy Commissioning Report
CLIENT: Yazan Hunjul
PROJECT NAME: 112
PROJECT NUMBER: 232
DATE OF VISIT: 2025-04-24
ENGINEER(s): Yazan Hunjul, Marc4
Your Kitchen Ventilation System has the following serviceable technology:
KITCHEN CANOPY AIR READINGS
EXTRACT AIR DATA
Drawing Number: 129
Location: Main Kitchen
Model: KVF
Total Design Airflow: 1.2 m³/s
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 40.0 Pa |  | 143.5 |  | 908.0 | 0.25 | 21.0%
Total Flowrate 0.25 m³/s
Percentage of Design 21.0%
SUPPLY AIR DATA
Drawing Number: 129
Location: Main Kitchen
Model: KVF
Total Supply Design Airflow: 1.3 m³/s
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
SUPPLY AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 40.0 Pa |  | 182.6 |  | 1154.86 | 0.32 | 25.0%
Total Flowrate 0.32 m³/s
Percentage of Design 25.0%
M.A.R.V.E.L. SYSTEM FOR KVF
Canopy 'Minimum' Air Flow Set Point % of Design | [6 empty] | 0
Canopy 'Idle' Air Flow Set % Of Design | [6 empty] | 1
Canopy 'Cook' Air Flow Set % Of Design | [6 empty] | 0
M.A.R.V.E.L. System Tested in 'Minimum' Mode | [6 empty] | ✓
M.A.R.V.E.L. System Tested in 'Idle' Mode | [6 empty] | ✓
M.A.R.V.E.L. System Tested in 'Cook' Mode | [6 empty] | ✓
Cook Mode Run Time (Seconds) | [6 empty] | 1
Testing of Canopy LIR-2 Sensors Successful | [6 empty] | ✓
M.A.R.V.E.L. System Override Temp Setpoint (°C) | [6 empty] | 0
Override Test on Halton HMI Successful | [6 empty] | ✓
Auto-Balance of M.A.R.V.E.L. System Successful | [6 empty] | ✓
EXTRACT AIR DATA
Drawing Number: 1.3
Location: Second Kitchen
Model: KVF
Total Design Airflow: 1.92 m³/s
Quantity of Canopy Sections: 2
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 50.0 Pa |  | 143.5 |  | 1015.0 | 0.28 | 15.0%
2 | 30.0 Pa |  | 143.5 |  | 786.0 | 0.22 | 11.0%
Total Flowrate 0.5 m³/s
Percentage of Design 26.1%
SUPPLY AIR DATA
Drawing Number: 1.3
Location: Second Kitchen
Model: KVF
Total Supply Design Airflow: 1.8 m³/s
Quantity of Canopy Sections: 2
Calculation: QV = Kf x √Pa
SUPPLY AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 50.0 Pa |  | 182.6 |  | 1291.18 | 0.36 | 20.0%
2 | 0.0 Pa |  | 121.7 |  | 0.0 | 0.0 | 0.0%
Total Flowrate 0.36 m³/s
Percentage of Design 20.0%
M.A.R.V.E.L. SYSTEM FOR KVF
Canopy 'Minimum' Air Flow Set Point % of Design | [6 empty] | 2
Canopy 'Idle' Air Flow Set % Of Design | [6 empty] | 0
Canopy 'Cook' Air Flow Set % Of Design | [6 empty] | 1
M.A.R.V.E.L. System Tested in 'Minimum' Mode | [6 empty] | ✓
M.A.R.V.E.L. System Tested in 'Idle' Mode | [6 empty] | ✓
M.A.R.V.E.L. System Tested in 'Cook' Mode | [6 empty] | ✓
Cook Mode Run Time (Seconds) | [6 empty] | 0
Testing of Canopy LIR-2 Sensors Successful | [6 empty] | ✓
M.A.R.V.E.L. System Override Temp Setpoint (°C) | [6 empty] | 0
Override Test on Halton HMI Successful | [6 empty] | ✓
Auto-Balance of M.A.R.V.E.L. System Successful | [6 empty] | ✓
EXTRACT AIR DATA
Drawing Number: 1.23
Location: Dishwash
Model: KSR-S
Total Design Airflow: 1.14 m³/s
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m³/h) |  | Flowrate (m³/h) | Flowrate (m³/s) | Percentage
1 | 0.0 Pa |  | 68.6 |  | 0.0 | 0.0 | 0.0%
Total Flowrate 0.0 m³/s
Percentage of Design 0.0%
RESULTS SUMMARY - EXTRACT AIR
Drawing Number |  | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
1.23 |  | 1.2 |  | 0.25 |  | 20.8%
1.23 |  | 1.92 |  | 0.5 |  | 26.0%
1.23 |  | 1.14 |  | 0.0 |  | 0.0%
TOTAL |  | 4.26 |  | 0.75 |  | 17.6%
RESULTS SUMMARY - SUPPLY AIR
Drawing Number |  | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
129 |  | 1.3 |  | 0.32 |  | 24.6%
1.3 |  | 1.8 |  | 0.36 |  | 20.0%
TOTAL |  | 3.1 |  | 0.68 |  | 21.9%
FINAL SYSTEM CHECKS
EDGE BOX
Edge Installed | [6 empty] | ✓
Edge ID | [6 empty] | 1.2
Edge 4G Status | [6 empty] | Online
LAN Connection Available | [6 empty] | No
Modbus Operation
ADDITIONAL NOTES
All Goode
e
Date |  | 2025-04-24
Print |  | Yazan Hunjul, Marc4
Sign