## Sheet1
COMMISSIONING REPORT
HOODS [ KVF UVF ]
Client: Defffe | [5 empty] | Date: 2024-08-27
Canopy Type(s): KVF UVF | [5 empty] | Location:
Drawing No.: efef
KVF main kitchen 1212 1 | [5 empty] | YES | NO
All Filters Are In Place | [5 empty] | YES
Hood Lights Are Working | [5 empty] | YES
Capture Jet Fan Is Working | [6 empty] | NO
KVF main kitchen 1212 1 MARVEL SYSTEM | [5 empty] | YES | NO
Display Touch Screen Tested For Correct Operation
Control Calculator Power Up And Tested For Correct Operation
Settings: 0 To 10 Vdc: 5, 4 To 20 Milli Amperes: 6
Exhaust Hood Abd Dampers Are Operational
Infrared Sensor ( Ir Sensor) Tested For Operation And Direction Adjusted |  |  |  |  | Achieved M3/h | YES | Percentage
Room Sensor Installed And Tested |  |  |  |  | 0.00 | 0.00 | NO
No Alarm On The Touch Screen
Airflows
KVF main kitchen 1212 1 Readings
Extract Air
No of Sections: 1
Section # | Number Of Filters | Manometer Reading | √ | K-Factor | Achieved M3/h | Design M3/H | Percentage
M1 | 4 | 100.0 | 10.00 | 268.88 | 2688.80 | 2000.0 | 134%
| TOTAL |  |  |  | 2688.80 | 2000.00 | 134%
Supply Air
Section # | Length Of Section | Manometer Reading | √ | K-Factor | Achieved M3/h | Design M3/H | Percentage
M1 | 1.5 | 20.0 pa | 4.47 | 486.9 | 816.61 | 1700.0 | 41%
UVF 2 | [5 empty] | YES | NO
Communication To All Uv Controllers Confirmed
Safety Interlock To Uv Door/Chambers Tested For Correct Operation
Safety Interlock To All Filters Tested For Correct Operation
Uv Operation Tested And Left Working
Airflows
UVF 2 Readings
Extract Air
No of Sections: 2 | Number Of Filters | Manometer Reading | √ | K-Factor | Achieved M3/h | Design M3/H | Percentage
| TOTAL |  |  |  | 0.00 | 0.00 | 0%
Section # | Number Of Filters | Manometer Reading | √ | K-Factor | Achieved M3/h | Design M3/H | Percentage
M1 | 0 | 0.0 | 0.00 | 0 | 0.00 | 0.0 | 0%
M2 | 0 | 0.0 | 0.00 | 0 | 0.00 | 0.0 | 0%
| TOTAL |  |  |  | 0.00 | 0.00 | 0%
Supply Air
Section # | Length Of Section | Manometer Reading | √ | K-Factor | Achieved M3/h | Design M3/H | Percentage
M1 | 0.0 | 0.0 pa | 0.00 | 0 | 0.00 | 0.0 | 0%