## Sheet
Canopy Commissioning Report
CLIENT:
PROJECT NAME:
PROJECT NUMBER:
DATE OF VISIT: 2025-05-07
ENGINEER(s):
Your Kitchen Ventilation System has the following serviceable technology:
KITCHEN CANOPY AIR READINGS
EXTRACT AIR DATA
Drawing Number | 1233
Location | Main Kitchen
Model | UVF
Design Flowrate (m³/s) | 1.2
Quantity of Sections | 1
Calculation | QV = Kf x √Pa
With M.A.R.V.E.L. | Yes
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) | K-Factor (m³/h) | Flowrate (m³/h) | Flowrate (m³/s) | Min (%) | Idle (%) | Design (m³/s)
1 | 30.0 Pa | 71.8 | 393.0 | 0.109 | 20.0% | 40.0% | 1.2
Total Flowrate: 0.109 m³/s
SUPPLY AIR DATA
Drawing Number | 1233
Location | Main Kitchen
Model | UVF
Design Airflow (m³/s) | 1.1
Quantity of Sections | 1
Calculation | QV = Kf x √Pa
With M.A.R.V.E.L. | Yes
SUPPLY AIR READINGS
Section # | T.A.B Point Reading (Pa) | K-Factor (m³/h) | Flowrate (m³/h) | Flowrate (m³/s) | Min (%) | Idle (%) | Design (m³/s)
1 | 0.0 Pa | 121.7 | 0.0 | 0.000 | 0.0% | 0.0% | 0.0
Total Flowrate: 0.000 m³/s
UV CAPTURE RAY SYSTEM FOR UVF
Quantity of Slaves per System | [5 empty] | 2
UV Pressure Setpoint (Pa) | [5 empty] | 20
Capture Jet Average Pressure Reading (Pa) | [5 empty] | 0
Airflow Proved on Each Controller | [5 empty] | ✓
Communication To All Canopy Controllers | [5 empty] | ✓
UV System Tested and Fully Operational | [5 empty] | ✓
All UV Safety Switches Tested | [5 empty] | ✓
All Filter Safety Switches Tested | [5 empty] | ✓
EXTRACT AIR DATA
Drawing Number | 1233
Location | Main Kitchen
Model | UVF
Design Flowrate (m³/s) | 1.2
Quantity of Sections | 1
With M.A.R.V.E.L. | Yes
EXTRACT AIR READINGS
RESULTS SUMMARY - EXTRACT AIR
Drawing Number | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
1233 | 1.200 |  | 0.109 |  | 9.1%
TOTAL | 1.200 |  | 0.109 |  | 9.1%
RESULTS SUMMARY - SUPPLY AIR
Drawing Number | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
1233 | 1.100 |  | 0.000 |  | 0.0%
TOTAL | 1.100 |  | 0.000 |  | 0.0%
FINAL SYSTEM CHECKS
EDGE BOX
Edge Installed
Edge ID
Edge 4G Status
LAN Connection Available
Modbus Operation
ADDITIONAL NOTES
Date | 2025-05-07
Print
Sign