## Sheet
Canopy Commissioning Report
CLIENT:
PROJECT NAME:
PROJECT NUMBER: 2332
DATE OF VISIT: 2025-01-23
ENGINEER(s):
Your Kitchen Ventilation System has the following serviceable technology:
KITCHEN CANOPY AIR READINGS
EXTRACT AIR DATA
Drawing Number: 2332-1212
Location: 1221
Model: KVF
Total Design Airflow: 1.8 M³/s
Quantity of Canopy Sections: 2
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m3 /h) |  | Flowrate (m3 /h) | Flowrate (m3 /s) | Percentage
1 | 40.0 pa |  | 215.4 |  | 1362.31 | 0.38 | 21.0%
2 | 50.0 pa |  | 143.6 |  | 1015.41 | 0.28 | 16.0%
Total Flowrate 0.66 M³/s
Total Percentage 36.7%
SUPPLY AIR DATA
2332-1212
Location: 1221
Model: KVF
Total Supply Design Airflow: 1.5 M³/s
Quantity of Canopy Sections: 2
Calculation: QV = Kf x √Pa
SUPPLY AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m3 /h) |  | Flowrate (m3 /h) | Flowrate (m3 /s) | Percentage
1 | 30.0 pa |  | 243.4 |  | 1333.16 | 0.37 | 25.0%
2 | 44.0 pa |  | 121.7 |  | 807.27 | 0.22 | 15.0%
Total Flowrate 0.59 m3/s
Total Percentage 40.0%
M.A.R.V.E.L. SYSTEM FOR KVF
Canopy 'Minimum' Air Flow Set Point % of Design | [6 empty] | 0
Canopy 'Idle' Air Flow Set % Of Design | [6 empty] | 2
Canopy 'Cook' Air Flow Set % Of Design | [6 empty] | 0
M.A.R.V.E.L. System Tested in 'Minimum' Mode | [6 empty] | ✓
M.A.R.V.E.L. System Tested in 'Idle' Mode | [6 empty] | ✓
M.A.R.V.E.L. System Tested in 'Cook' Mode | [6 empty] | ✓
Cook Mode Run Time (Seconds) | [6 empty] | 2
Testing of Canopy LIR-2 Sensors Successful | [6 empty] | ✓
M.A.R.V.E.L. System Override Temp Setpoint (°C) | [6 empty] | 0
Override Test on Halton HMI Successful | [6 empty] | ✓
Auto-Balance of M.A.R.V.E.L. System Successful | [6 empty] | ✓
EXTRACT AIR DATA
Drawing Number: 2332-323
Location: cddccd
Model: KCH-I
Total Design Airflow: 1.5 M³/s
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Section # | T.A.B Point Reading (Pa) |  | K-Factor (m3 /h) |  | Flowrate (m3 /h) | Flowrate (m3 /s) | Percentage
1 | 32.0 pa |  | 143.6 |  | 812.32 | 0.23 | 15.0%
Total Flowrate 0.23 M³/s
Total Percentage 15.0%
RESULTS SUMMARY - EXTRACT AIR
Drawing Number |  | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
2332-1212 |  | 1.8 |  | 0.66 |  | 36.7%
2332-323 |  | 1.5 |  | 0.23 |  | 15.3%
TOTAL |  | 3.3 |  | 0.89 |  | 27.0%
RESULTS SUMMARY - SUPPLY AIR
Drawing Number |  | Design Flow Rate (m³/s) |  | Actual Flowrate (m³/s) |  | Percentage of Design
2332-1212 |  | 1.5 |  | 0.59 |  | 39.3%
TOTAL |  | 1.5 |  | 0.59 |  | 39.3%
ADDITIONAL NOTES
dfdafe
fefafef
Date |  | 2025-01-23
Print
Sign