## Sheet
Canopy Commissioning Report
CLIENT:
PROJECT NAME:
PROJECT NUMBER:
DATE OF VISIT: 2024-10-01
ENGINEER(s): Mike, Yazan
KITCHEN CANOPY AIR READINGS
EXTRACT AIR DATA
Drawing Number: 1212
Location: Main Kitchen
Model: KCH-I
Quantity of Canopy Sections: 2
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Module # | T.A.B Point Reading (Pa) | K-Factor (m3 /h) | Flowrate (m3 /h) | Flowrate (m3 /s) | Percentage
1 | 300.0 pa | 215.4 | 3730.84 | 400.0 | 9.0%
2 | 322.0 pa | 143.6 | 2576.81 | 323.0 | 8.0%
Total Flowrate 723.0 m3/s
Total Percentage 11.0%
EXTRACT AIR DATA
Drawing Number:
Location:
Model: KVI
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Module # | T.A.B Point Reading (Pa) | K-Factor (m3 /h) | Flowrate (m3 /h) | Flowrate (m3 /s) | Percentage
1 | 23.0 pa | 71.8 | 344.34 | 32.0 | 11.0%
Total Flowrate 32.0 m3/s
Total Percentage 9.0%
EXTRACT AIR DATA
Drawing Number:
Location:
Model: KVI
Quantity of Canopy Sections: 1
Calculation: QV = Kf x √Pa
EXTRACT AIR READINGS
Module # | T.A.B Point Reading (Pa) | K-Factor (m3 /h) | Flowrate (m3 /h) | Flowrate (m3 /s) | Percentage
1 | 322.0 pa | 71.8 | 1288.4 | 33.0 | 39.0%
Total Flowrate 33.0 m3/s
Total Percentage 3.0%